## AC UPS
INPUT DATA
Vn |  | 110 | Standard battery size (AH) | 1 | 161
% Vmax | 20 | 132 | time to recharge the battery to 95% of capacity (hours) | 8
% Vmin | 10 | 99 | Continuous DC load (A) | 98.8142
operation Period (min) |  | 60 | Battery Chargers Sizing (A) | 143.0892
Battery Equalizing Voltage |  | 1.47
derating factor (Kt) |  | 1.77
Temperature factor (Tt) |  | 1.08
aging factor |  | 1.25
design margin | 1.1 | 1.2222
State of charge | 0.9
% load supplied by battery |  | 50
load Power (w) |  | 7500
power factor |  | 0.8
inverter efficiency |  | 0.92
Number of cells |  | 90
final voltage |  | 1.1
input inverter power (w) |  | 4891.3043
maximum current (A) |  | 49.4071
Battery size (AH) |  | 144.2935

## DC UPS
INPUT DATA
Vn |  | 110 |  |  |  | Required Battery Size (AH) | 90.3115 | Standard battery size (AH) | 1 | 161
% Vmax | 20 | 132 | [5 empty] | Time to recharge the battery to 95% of capacity (hours) |  | 8
% Vmin | 10 | 99 | [5 empty] | KVA Required |  | 3483
operation Period (min) | first min | 1 | 6102 | Power (W) |  |  |  | Continuous DC load (A) |  | 31.6636
| first< t <last | 118 | 2322 |  |  |  |  | Battery Chargers Sizing (A) |  | 82.2714
| last min | 1 | 15552
Battery Equalizing Voltage |  | 1.47
aging factor |  | 1.25
design margin | 1.1 | 1.2222
State of charge | 0.9
% load supplied by battery |  | 50
power factor |  | 0.8
Number of cells |  | 90
final voltage |  | 1.1
Load Power (W) | first min | 2491.56 | Maximum Current (A) |  | 25.1673
| first< t <last | 1393.2 |  |  | 14.0727
| last min | 4192.56 |  |  | 42.3491
derating factor (Kt) | first min | 0.559
| first< t <last | 2.645
| last min | 2.664
Temperature factor (Tt) | first min | 1.14
| first< t <last | 1.09
| last min | 1.09
A0 | 0 |  | Load Changes (A) | A1-A0 | 25.1673 | first min charging (AH) | 16.0381
A1 | 25.1673 |  |  | A2-A1 | -11.0945
A2 | 14.0727 |  |  | A3-A2 | 28.2764 | Discharging status (AH) | 59.113
A3 | 42.3491