## Cover
AC UPS LOAD LIST-ASU
Document Title
1 of 5
Page No.
Document Number :
TYPE
SIZE
GROUP
DOC. NO.
Rev.
JOB NO.

## Revision Index
SHEET | REVISION |  |  |  |  | SHEET | REVISION
| D0 | D1 | D2 | D3 | D4 |  | D0 | D1 | D2 | D3 | D4
1 | X |  |  |  |  | 21
2 | X |  |  |  |  | 22
3 | X |  |  |  |  | 23
4 | X |  |  |  |  | 24
5 | X |  |  |  |  | 25
6 | [5 empty] | 26
7 | [5 empty] | 27
8 | [5 empty] | 28
9 | [5 empty] | 29
10 | [5 empty] | 30
11 | [5 empty] | 31
12 | [5 empty] | 32
13 | [5 empty] | 33
14 | [5 empty] | 34
15 | [5 empty] | 35
16 | [5 empty] | 36
17 | [5 empty] | 37
18 | [5 empty] | 38
19 | [5 empty] | 39
20 | [5 empty] | 40

## TOTAL
UPS DISTRIBUTION BOARD INCOMING TOTAL LOAD
Panel Tag |  |  | Description |  | P | Q | S | PF | I | MCCB
[5 empty] | [kW] | [kVAr] | kVA |  | [A] | Rating
1 | EE-DP-15-01 |  | Distribution Board |  | 44.995 | 14.7891 | 47.3632 | 0.95 | 430.5742 | 1250
|  |  |  | Selected size of the UPS = |  | 100 | kVA | @ | 0.95 | Power factor
| (1) | As the power consumption of instrument panels related to units no. 2, 3, and 4 are not clear, the selected size is chosen approximately.
[11 empty] | #REF! | #REF!
| (2) | Size of battery bank shall be calculated based on 30 Minutes flat load profile (by vendor). | [8 empty] | #REF! | #REF!
| (3) | Battery shall be capable to supply 120% of maximum initial load for this period.
|  | 0 | 2
|  | 0.25 | 2
|  | 0.32 | 2
|  | 0.4 | 2
|  | 0.8 | 2
|  | 1 | 2
|  | 1.25 | 2
|  | 2 | 3.2
|  | 3.2 | 4
|  | 4 | 6.3
|  | 6.3 | 6
|  | 6 | 10
|  | 10 | 16
|  | 16 | 20
|  | 20 | 25
|  | 25 | 32
|  | 32 | 50
|  | 50 | 63
|  | 63 | 80
|  | 80 | 100
|  | 100 | 125
|  | 125 | 160
|  | 160 | 200
|  | 200 | 250
|  | 250 | 315
315
3 of 5
Page No.
TYPE
SIZE
GROUP
DOC. NO.
Rev.
JOB NO.

## LOAD LIST
LOAD LIST SEQ. NO. | Revision |  | Duty |  |  |  |  | Feeder |  |  |  |  | Remarks
|  | Description/Tag |  | Circuit | Volt | P | Q | PF | Current | Switch | Control | Location
|  |  |  | Loading | (V) | (W) | (VAr) | (cos ϕ) | (A) | Rating | Code
1 | D0 | Paging System | C | 100% | 110 | 3000 | 986.0523 | 0.95 | 28.7081 | 50 |  | AUX |  | 3000 | 986.0523
2 | D0 | Radio base station | C | 100% | 110 | 300 | 98.6052 | 0.95 | 2.8708 | 4 |  | AUX |  | 300 | 98.6052
3 | D0 | Voice Radio System | C | 100% | 110 | 300 | 98.6052 | 0.95 | 2.8708 | 4 |  | AUX |  | 300 | 98.6052
4 | D0 | CCTV 46" MONITOR 1 | C | 100% | 110 | 100 | 32.8684 | 0.95 | 0.95694 | 2 |  | CCR |  | 100 | 32.8684
5 | D0 | CCTV 46" MONITOR 1 | C | 100% | 110 | 100 | 32.8684 | 0.95 | 0.95694 | 2 |  | CCR |  | 100 | 32.8684
6 | D0 | Plant DCS System | C | 50% | 110 | 6400 | 2103.5783 | 0.95 | 61.244 | 80 |  | AUX |  | 3200 | 1051.7891
7 | D0 | Plant DCS System | C | 50% | 110 | 6400 | 2103.5783 | 0.95 | 61.244 | 80 |  | AUX |  | 3200 | 1051.7891
8 | D0 | F&G System | C | 50% | 110 | 3000 | 986.0523 | 0.95 | 28.7081 | 50 |  | AUX |  | 1500 | 493.0262
9 | D0 | F&G System | C | 50% | 110 | 3000 | 986.0523 | 0.95 | 28.7081 | 50 |  | AUX |  | 1500 | 493.0262
10 | D0 | IG panel 1 | C | 100% | 110 | 1000 | 328.6841 | 0.95 | 9.5694 | 16 |  | CCR | HSE | 1000 | 328.6841
11 | D0 | IG panel 2 | C | 100% | 110 | 1000 | 328.6841 | 0.95 | 9.5694 | 16 |  | SUB1 | HSE | 1000 | 328.6841
12 | D0 | IG panel 3 | C | 100% | 110 | 1000 | 328.6841 | 0.95 | 9.5694 | 16 |  | SUB2 | HSE | 1000 | 328.6841
13 | D0 | CCTV work station | C | 100% | 110 | 360 | 118.3263 | 0.95 | 3.445 | 6.3 |  | CCR | CONTROL BUILDING | 360 | 118.3263
14 | D0 | CCTV work station | C | 100% | 110 | 360 | 118.3263 | 0.95 | 3.445 | 6.3 |  | CCR | CONTROL BUILDING | 360 | 118.3263
15 | D0 | PDCS work station1 | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  | CCR | CONTROL BUILDING | 500 | 164.3421
16 | D0 | PDCS work station2 | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  | CCR | CONTROL BUILDING | 500 | 164.3421
17 | D0 | CCTV System | C | 100% | 110 | 3000 | 986.0523 | 0.95 | 28.7081 | 50 |  | CCR | CONTROL BUILDING | 3000 | 986.0523
18 | D0 | PDCS System | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  | AUX | CONTROL BUILDING | 2000 | 657.3682
19 | D0 | PDCS System - CABINET 33KV SUBSTATION | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  |  |  | 2000 | 657.3682
20 | D0 | PDCS System - CABINET 11/6/0.4 KV SUBSTATION | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  |  |  | 2000 | 657.3682
21 | D0 | PDCS System - CABINET 11/6/0.4 KV SUBSTATION | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  |  |  | 2000 | 657.3682
22 | D0 | PDCS System CONSOLE | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  | CCR | CONTROL BUILDING | 500 | 164.3421
23 | D0 | Damavand DCS RIO - HOLD | C | 100% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
24 | D0 | ASU Units #2 PCSS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
25 | D0 | ASU Units #2 PCSS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
26 | D0 | ASU Units #3 PCSS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
27 | D0 | ASU Units #3 PCSS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
28 | D0 | ASU Units #4 PCSS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
29 | D0 | ASU Units #4 PCSS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
30 | D0 | ASU Unit #2 DCS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
31 | D0 | ASU Unit #2 DCS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
32 | D0 | ASU Unit #3 DCS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
33 | D0 | ASU Unit #3 DCS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
34 | D0 | ASU Unit #4 DCS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
35 | D0 | ASU Unit #4 DCS System - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  | AUX | By Damavand | 0 | 0
36 | D0 | ASU Unit #2 PDCS System | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  | AUX |  | 2000 | 657.3682
37 | D0 | ASU Unit #3 PDCS System | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  | AUX |  | 2000 | 657.3682
38 | D0 | ASU Unit #4 PDCS System | C | 100% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  | AUX |  | 2000 | 657.3682
39 | D0 | Supervisor Work Station | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  | CCR |  | 500 | 164.3421
40 | D0 | Manager Work Station | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  | CCR |  | 500 | 164.3421
41 | D0 | F&G panel - CONTROL ROOM | C | 100% | 110 | 1500 | 493.0262 | 0.95 | 14.3541 | 20 |  | CCR | CONTROL BUILDING | 1500 | 493.0262
42 | D0 | F&G panel -LER SIAD | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  | LER |  | 500 | 164.3421
43 | D0 | ASU Unit No.2 equipment - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
44 | D0 | ASU Unit No.2 equipment - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
45 | D0 | ASU Unit No.3 equipment - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
46 | D0 | ASU Unit No.3 equipment - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
47 | D0 | ASU Unit No.4 equipment - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
48 | D0 | ASU Unit No.4 equipment - HOLD | C | 50% | 110 |  | 0 | 0.95 | 0 | 2 |  |  | By Damavand | 0 | 0
49 | D0 | F&G panel - STORAGE AREA | C | 100% | 110 | 500 | 164.3421 | 0.95 | 4.7847 | 6.3 |  |  |  | 500 | 164.3421
50 | D0 | Plant DCS RIO | C | 50% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  |  |  | 1000 | 328.6841
51 | D0 | Plant DCS RIO | C | 50% | 110 | 2000 | 657.3682 | 0.95 | 19.1388 | 25 |  |  |  | 1000 | 328.6841
52 | D0 | Plant DCS System IRP Panel | C | 100% | 110 | 1000 | 328.6841 | 0.95 | 9.5694 | 16 |  |  |  | 1000 | 328.6841
53 | D0 | F&G panel - 33KV SUBSTATION | C | 50% | 110 | 750 | 246.5131 | 0.95 | 7.177 | 10 | ` | SUB1 |  | 375 | 123.2565
54 | D0 | Magnetic Flow Meters | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
55 | D0 | Magnetic Flow Meters | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
56 | D0 | Magnetic Flow Meters | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
57 | D0 | Magnetic Flow Meters | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
58 | D0 | Ultrasonic Flow Meters | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
59 | D0 | Radar Level Instrument | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
60 | D0 | Radar Level Instrument | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
61 | D0 | Radar Level Instrument | C | 100% | 110 | 25 | 8.2171 | 0.95 | 0.23923 | 2 |  |  |  | 25 | 8.2171
62 | D0 | F&G panel - 11/6/0.4 KV SUBSTATION | C | 100% | 110 | 1000 | 328.6841 | 0.95 | 9.5694 | 16 |  | SUB2 |  | 1000 | 328.6841
63 | D0 | Telephone system - PABX | C | 100% | 110 | 1500 | 493.0262 | 0.95 | 14.3541 | 20 |  | AUX |  | 1500 | 493.0262
|  | Total Load |  |  |  | 44995 | 14789.1413
* NOTE: HOLD ITEMS SHALL BE CLARIFIED BY DAMAVAND