1. Summary
    Ventilation Sizing Method 	 Sum of Space OA Airflows	
    Design Ventilation Airflow Rate 	 0	CFM

2. Space Ventilation Analysis Table
 	 	Floor	 	Maximum	Required	Required	Required	Required	Uncorrected	
 	 	Area	Maximum	Supply Air	Outdoor Air	Outdoor Air	Outdoor Air	Outdoor Air	Outdoor Air	
Zone Name / Space Name	Mult.	(ft²)	Occupants	(CFM)	(CFM/person)	(CFM/ft²)	(CFM)	(% of supply)	(CFM)	
g	 	 	 	 	 	 	 	 	 	
    g-bd1	1	172.2	2.0	336.7	0.00	0.00	0.0	0.0	0.0	
    g-liv	1	1205.6	14.0	2425.0	0.00	0.00	0.0	0.0	0.0	
1ST	 	 	 	 	 	 	 	 	 	
    1st-bd1	1	204.5	2.0	415.0	0.00	0.00	0.0	0.0	0.0	
    1st-bd2	1	75.3	2.0	228.8	0.00	0.00	0.0	0.0	0.0	
    1st-bd3	1	64.6	1.0	71.1	0.00	0.00	0.0	0.0	0.0	
    1st-liv	1	818.1	8.0	2064.0	0.00	0.00	0.0	0.0	0.0	
    1st-tvroom	1	645.8	8.0	1281.2	0.00	0.00	0.0	0.0	0.0	
2ND	 	 	 	 	 	 	 	 	 	
    2nd-bd1	1	269.1	2.0	483.4	0.00	0.00	0.0	0.0	0.0	
    2nd-bd2	1	236.8	2.0	572.4	0.00	0.00	0.0	0.0	0.0	
    2nd-liv	1	952.6	10.0	1525.6	0.00	0.00	0.0	0.0	0.0	
Totals (incl. Space Multipliers)	 	 	 	9403.0	 	 	 	 	0.0	

g	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Sep 1500	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   91.2 °F / 64.0 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
ZONE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	503 ft²	19530	-	503 ft²	-	-	
Wall Transmission	1144 ft²	5367	-	1144 ft²	7891	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	503 ft²	2718	-	503 ft²	14067	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	1378 ft²	0	-	1378 ft²	1504	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	2756 W	9402	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	16	3680	1922	0	0	0	
Infiltration	-	3609	-1309	-	19063	-2	
Miscellaneous	-	1000	1000	-	0	0	
Safety Factor	10% / 10%	4530	161	20%	8505	0	
>> Total Zone Loads	-	49834	1774	-	51029	-3	

1ST	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Sep 1600	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   92.0 °F / 64.2 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
ZONE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	696 ft²	28277	-	696 ft²	-	-	
Wall Transmission	1323 ft²	6740	-	1323 ft²	9130	-	
Roof Transmission	323 ft²	801	-	323 ft²	2216	-	
Window Transmission	696 ft²	4070	-	696 ft²	19437	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	183 ft²	202	-	183 ft²	366	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	3617 W	12340	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	21	4829	2522	0	0	0	
Infiltration	-	4986	-1683	-	25020	8	
Miscellaneous	-	293	293	-	0	0	
Safety Factor	10% / 10%	6254	113	20%	11234	2	
>> Total Zone Loads	-	68792	1245	-	67402	10	

2ND	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Aug 1600	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   96.8 °F / 67.0 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
ZONE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	431 ft²	12212	-	431 ft²	-	-	
Wall Transmission	1451 ft²	8532	-	1451 ft²	10009	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	431 ft²	3542	-	431 ft²	12093	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	2917 W	9953	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	14	3220	1682	0	0	0	
Infiltration	-	5145	-388	-	20180	-8	
Miscellaneous	-	293	293	-	0	0	
Safety Factor	10% / 10%	4290	159	20%	8456	-2	
>> Total Zone Loads	-	47186	1745	-	50738	-9	

TABLE 1.1.A.    COMPONENT LOADS FOR SPACE  '' g-bd1 ''  IN ZONE  '' g ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jul 1700	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   95.9 °F / 66.8 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	72 ft²	1320	-	72 ft²	-	-	
Wall Transmission	216 ft²	1537	-	216 ft²	1491	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	72 ft²	585	-	72 ft²	2027	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	172 ft²	0	-	172 ft²	441	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	344 W	1175	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	2	460	240	0	0	0	
Infiltration	-	584	-42	-	2383	0	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	566	20	20%	1268	0	
>> Total Zone Loads	-	6227	218	-	7610	0	

TABLE 1.1.B.    ENVELOPE LOADS FOR SPACE  '' g-bd1 ''  IN ZONE  '' g ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	144	0.121	-	1293	-	995	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	72	0.121	-	244	-	496	
    WINDOW 1	72	0.492	0.743	585	1320	2027	

TABLE 1.2.A.    COMPONENT LOADS FOR SPACE  '' g-liv ''  IN ZONE  '' g ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Sep 1500	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   91.2 °F / 64.0 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	431 ft²	18655	-	431 ft²	-	-	
Wall Transmission	927 ft²	4192	-	927 ft²	6400	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	431 ft²	2326	-	431 ft²	12040	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	1206 ft²	0	-	1206 ft²	1063	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	2411 W	8227	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	14	3220	1682	0	0	0	
Infiltration	-	3157	-1145	-	16680	-2	
Miscellaneous	-	1000	1000	-	0	0	
Safety Factor	10% / 10%	4078	154	20%	7236	0	
>> Total Zone Loads	-	44853	1689	-	43419	-2	

TABLE 1.2.B.    ENVELOPE LOADS FOR SPACE  '' g-liv ''  IN ZONE  '' g ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	291	0.121	-	2032	-	2005	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	25	0.121	-	59	-	175	
    WINDOW 1	175	0.489	0.743	941	2114	4871	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	523	0.121	-	1512	-	3610	
S  EXPOSURE	 	 	 	 	 	 	
    WALL	88	0.121	-	589	-	609	
    WINDOW 1	69	0.489	0.743	373	4476	1932	
    WINDOW 2	187	0.492	0.743	1012	12065	5237	

TABLE 2.1.A.    COMPONENT LOADS FOR SPACE  '' 1st-bd1 ''  IN ZONE  '' 1ST ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jul 1700	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   95.9 °F / 66.8 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	102 ft²	1869	-	102 ft²	-	-	
Wall Transmission	222 ft²	1597	-	222 ft²	1529	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	102 ft²	824	-	102 ft²	2855	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	108 ft²	139	-	108 ft²	215	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	409 W	1396	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	2	460	240	0	0	0	
Infiltration	-	693	-51	-	2830	1	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	698	19	20%	1486	0	
>> Total Zone Loads	-	7676	208	-	8914	1	

TABLE 2.1.B.    ENVELOPE LOADS FOR SPACE  '' 1st-bd1 ''  IN ZONE  '' 1ST ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	152	0.121	-	1360	-	1047	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	70	0.121	-	237	-	481	
    WINDOW 1	102	0.489	0.743	824	1869	2855	

TABLE 2.2.A.    COMPONENT LOADS FOR SPACE  '' 1st-bd2 ''  IN ZONE  '' 1ST ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jun 1800	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   91.0 °F / 64.2 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	75 ft²	1703	-	75 ft²	-	-	
Wall Transmission	135 ft²	432	-	135 ft²	928	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	75 ft²	457	-	75 ft²	2105	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	75 ft²	85	-	75 ft²	151	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	151 W	514	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	2	460	240	0	0	0	
Infiltration	-	194	-62	-	1042	0	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	385	18	20%	845	0	
>> Total Zone Loads	-	4231	196	-	5072	0	

TABLE 2.2.B.    ENVELOPE LOADS FOR SPACE  '' 1st-bd2 ''  IN ZONE  '' 1ST ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	80	0.121	-	231	-	550	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	55	0.121	-	202	-	379	
    WINDOW 1	75	0.490	0.743	457	1703	2105	

TABLE 2.3.A.    COMPONENT LOADS FOR SPACE  '' 1st-bd3 ''  IN ZONE  '' 1ST ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jul 1600	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   96.8 °F / 67.0 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	0 ft²	0	-	0 ft²	-	-	
Wall Transmission	69 ft²	265	-	69 ft²	475	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	0 ft²	0	-	0 ft²	0	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	129 W	441	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	1	230	120	0	0	0	
Infiltration	-	228	-16	-	894	0	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	116	10	20%	274	0	
>> Total Zone Loads	-	1279	115	-	1643	0	

TABLE 2.3.B.    ENVELOPE LOADS FOR SPACE  '' 1st-bd3 ''  IN ZONE  '' 1ST ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	69	0.121	-	265	-	475	

TABLE 2.4.A.    COMPONENT LOADS FOR SPACE  '' 1st-liv ''  IN ZONE  '' 1ST ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Sep 1500	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   91.2 °F / 64.0 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	307 ft²	19058	-	307 ft²	-	-	
Wall Transmission	659 ft²	3379	-	659 ft²	4549	-	
Roof Transmission	323 ft²	755	-	323 ft²	2216	-	
Window Transmission	307 ft²	1656	-	307 ft²	8570	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	1636 W	5582	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	8	1840	961	0	0	0	
Infiltration	-	2143	-761	-	11318	4	
Miscellaneous	-	293	293	-	0	0	
Safety Factor	10% / 10%	3471	49	20%	5331	1	
>> Total Zone Loads	-	38176	543	-	31984	4	

TABLE 2.4.B.    ENVELOPE LOADS FOR SPACE  '' 1st-liv ''  IN ZONE  '' 1ST ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	276	0.121	-	796	-	1901	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	16	0.121	-	37	-	111	
    WINDOW 1	15	0.493	0.743	82	182	424	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	292	0.121	-	2040	-	2013	
S  EXPOSURE	 	 	 	 	 	 	
    WALL	76	0.121	-	506	-	523	
    WINDOW 1	69	0.489	0.743	373	4476	1932	
    WINDOW 2	223	0.489	0.743	1201	14400	6215	
H  EXPOSURE	 	 	 	 	 	 	
    ROOF	323	0.120	-	755	-	2216	

TABLE 2.5.A.    COMPONENT LOADS FOR SPACE  '' 1st-tvroom ''  IN ZONE  '' 1ST ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jul 1700	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   95.9 °F / 66.8 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	211 ft²	9962	-	211 ft²	-	-	
Wall Transmission	239 ft²	1441	-	239 ft²	1649	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	211 ft²	1705	-	211 ft²	5907	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	1292 W	4407	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	8	1840	961	0	0	0	
Infiltration	-	2189	-160	-	8936	3	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	2154	80	20%	3298	1	
>> Total Zone Loads	-	23698	881	-	19790	3	

TABLE 2.5.B.    ENVELOPE LOADS FOR SPACE  '' 1st-tvroom ''  IN ZONE  '' 1ST ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	119	0.121	-	431	-	823	
    WINDOW 1	87	0.491	0.743	706	3491	2448	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	11	0.121	-	38	-	77	
    WINDOW 1	36	0.491	0.743	292	660	1012	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	109	0.121	-	972	-	749	
    WINDOW 1	87	0.491	0.743	706	5811	2448	

TABLE 3.1.A.    COMPONENT LOADS FOR SPACE  '' 2nd-bd1 ''  IN ZONE  '' 2ND ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jul 1700	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   95.9 °F / 66.8 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	102 ft²	1869	-	102 ft²	-	-	
Wall Transmission	285 ft²	2226	-	285 ft²	1967	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	102 ft²	824	-	102 ft²	2855	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	538 W	1836	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	2	460	240	0	0	0	
Infiltration	-	912	-74	-	3723	-1	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	813	17	20%	1709	0	
>> Total Zone Loads	-	8940	183	-	10254	-2	

TABLE 3.1.B.    ENVELOPE LOADS FOR SPACE  '' 2nd-bd1 ''  IN ZONE  '' 2ND ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	226	0.121	-	2026	-	1560	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	59	0.121	-	200	-	407	
    WINDOW 1	102	0.489	0.743	824	1869	2855	

TABLE 3.2.A.    COMPONENT LOADS FOR SPACE  '' 2nd-bd2 ''  IN ZONE  '' 2ND ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Jul 1500	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   95.9 °F / 66.8 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	157 ft²	4496	-	157 ft²	-	-	
Wall Transmission	273 ft²	1026	-	273 ft²	1882	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	157 ft²	1223	-	157 ft²	4419	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	474 W	1616	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	2	460	240	0	0	0	
Infiltration	-	803	-66	-	3276	-1	
Miscellaneous	-	0	0	-	0	0	
Safety Factor	10% / 10%	962	17	20%	1916	0	
>> Total Zone Loads	-	10586	191	-	11493	-2	

TABLE 3.2.B.    ENVELOPE LOADS FOR SPACE  '' 2nd-bd2 ''  IN ZONE  '' 2ND ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	176	0.121	-	683	-	1214	
    WINDOW 1	51	0.497	0.743	402	2251	1452	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	83	0.121	-	276	-	573	
    WINDOW 1	78	0.491	0.743	607	1441	2194	
S  EXPOSURE	 	 	 	 	 	 	
    WALL	14	0.121	-	68	-	95	
    WINDOW 1	27	0.500	0.743	214	804	773	

TABLE 3.3.A.    COMPONENT LOADS FOR SPACE  '' 2nd-liv ''  IN ZONE  '' 2ND ''	
 	DESIGN COOLING	DESIGN HEATING	
 	COOLING DATA AT Aug 1600	HEATING DATA AT DES HTG	
 	COOLING OA DB / WB   96.8 °F / 67.0 °F	HEATING OA DB / WB   13.0 °F / 12.0 °F	
 	OCCUPIED T-STAT 75.0 °F	OCCUPIED T-STAT 70.0 °F	
 	 	Sensible	Latent	 	Sensible	Latent	
SPACE LOADS	Details	(BTU/hr)	(BTU/hr)	Details	(BTU/hr)	(BTU/hr)	
Window & Skylight Solar Loads	172 ft²	6371	-	172 ft²	-	-	
Wall Transmission	893 ft²	5416	-	893 ft²	6160	-	
Roof Transmission	0 ft²	0	-	0 ft²	0	-	
Window Transmission	172 ft²	1411	-	172 ft²	4819	-	
Skylight Transmission	0 ft²	0	-	0 ft²	0	-	
Door Loads	0 ft²	0	-	0 ft²	0	-	
Floor Transmission	0 ft²	0	-	0 ft²	0	-	
Partitions	0 ft²	0	-	0 ft²	0	-	
Ceiling	0 ft²	0	-	0 ft²	0	-	
Overhead Lighting	1905 W	6500	-	0	0	-	
Task Lighting	0 W	0	-	0	0	-	
Electric Equipment	0 W	0	-	0	0	-	
People	10	2300	1201	0	0	0	
Infiltration	-	3361	-253	-	13180	-5	
Miscellaneous	-	293	293	-	0	0	
Safety Factor	10% / 10%	2565	124	20%	4832	-1	
>> Total Zone Loads	-	28217	1365	-	28991	-6	

TABLE 3.3.B.    ENVELOPE LOADS FOR SPACE  '' 2nd-liv ''  IN ZONE  '' 2ND ''	
 	 	 	 	COOLING	COOLING	HEATING	
 	Area	U-Value	Shade	TRANS	SOLAR	TRANS	
 	(ft²)	(BTU/(hr-ft²-°F))	Coeff.	(BTU/hr)	(BTU/hr)	(BTU/hr)	
E  EXPOSURE	 	 	 	 	 	 	
    WALL	263	0.121	-	975	-	1817	
    WINDOW 1	84	0.491	0.743	691	3359	2361	
N  EXPOSURE	 	 	 	 	 	 	
    WALL	10	0.121	-	31	-	68	
    WINDOW 1	18	0.511	0.743	154	273	526	
W  EXPOSURE	 	 	 	 	 	 	
    WALL	351	0.121	-	3028	-	2421	
S  EXPOSURE	 	 	 	 	 	 	
    WALL	269	0.121	-	1382	-	1854	
    WINDOW 1	69	0.489	0.743	566	2739	1932